**STEINEL Professional Aanwezigheidsmelder**

**Hallway**

**COM2 - Inbouw**

Dimensions (L x W x H): 67 x 103 x 103 mm; With motion detector: Ja; Manufacturer's Warranty: 5 jaar; Settings via: Bluetooth; With remote control: Nee; Version: COM2 - Inbouw; PU1, EAN: 4007841058005; Type: Aanwezigheidsmelder; Application, place: Binnen; Application, room: Binnen, hal / gang; Colour: wit; Colour, RAL: 9003; Includes corner wall mount: Nee; Installation site: plafond; Installation: In de muur, Plafond; IP-rating: IP20; Ambient temperature: van -20 tot 50 °C; Materiaal: kunststof; Mains power supply: 220 – 240 V / 50 – 60 Hz; Switching output 1, resistive: 2000 W; Switching output 1, number of LEDs / fluorescent lamps: 8 st; Switching output 1, floating: Nee; Switching output 2, resistive: 230 W; Switching output 2, floating: Ja; Fluorescent lamps, electronic ballast: 1500 W; Fluorescent lamps, uncorrected: 1000 VA; Fluorescent lamps, series-corrected: 400 VA; Fluorescent lamps, parallel-corrected: 1000 VA; Switching output 1, low-voltage halogen lamps: 2000 VA; LED lamps < 2 W: 100 W; LED lamps > 2 W < 8 W: 300 W; LED lamps > 8 W: 600 W; Capacitive load in μF: 176 µF; Power consumption: 0,7 W; Technology, sensors: Hoogfrequente straling, Lichtsensor; Mounting height: 2,00 – 4,00 m; Mounting height max.: 4,00 m; Optimum mounting height: 2,8 m; HF-system: 5,8 GHz; Detection: evt. door glas, hout en snelbouwwanden; Detection angle: Gang, 360 °; Angle of aperture: 140 °; Sneak-by guard: Ja; Capability of masking out individual segments: Nee; Electronic scalability: Ja; Mechanical scalability: Nee; Reach, radial: 25 x 3 m (75 m²); Reach, tangential: 25 x 3 m (75 m²); Transmitter power: < 1 mW; Functions: Parameterinstelling voor groepen, (Half-) automatisch, Lichtscène, Handmatig ON / ON-OFF, Buurgroepfunctie, Normaal- / testbedrijf; Twilight setting: 2 – 2000 lx; Time setting: 10 sec. – 60 min; Basic light level function: Nee; Main light adjustable: Nee; Twilight setting TEACH: Ja; Constant-lighting control: Nee; Interconnection: Ja; Type of interconnection: Master/master, Master/slave; Interconnection via: Bluetooth; Product category: Aanwezigheidsmelder

**Fabrikant** Steinel

**art.nr.** 058005

**Bestelaanduiding** Hallway COM2 - Inbouw

Leveren, monteren en bedrijfsklaar instellen