**STEINEL Professional Sensor-LED-binnenlamp**

**RS PRO 5100 SC 5C**

**5 Core (5-draads doorvoerbedrading)**

Dimensions (L x W x H): 1370 x 87 x 58 mm; With motion detector: Ja; Manufacturer's Warranty: 5 jaar; Settings via: Bluetooth; Version: 5 Core (5-draads doorvoerbedrading); PU1, EAN: 4007841079185; Colour: grijs; Installation site: wand, plafond; Installation: Wand, Plafond, Op de muur; Impact resistance: IK07; IP-rating: IP65; Protection class: II; Ambient temperature: van -20 tot 40 °C; Housing material: kunststof; Cover material: Kunststof gestructureerd; Mains power supply: 220 – 240 V / 50 – 60 Hz; Power consumption: 0,41 W; Mounting height max.: 4,00 m; Electronic scalability: Ja; Transmitter power: < 1 mW; Luminous flux total product: 4250 lm; Total product efficiency: 137 lm/W; Colour temperature: 4000 K; Colour variation LED: SDCM3; Lamp: Led niet vervangbaar; LED cooling system: Passive Thermo Control; Twilight setting: 2 – 2000 lx; Time setting: 5 sec. – 60 min; Basic light level function: Ja; Basic light level function time: 1-60 min.; Main light adjustable: 0 - 100 %; Interconnection: Ja; Interconnection via: Bluetooth Mesh; Lifetime LED according to IEC-62717 (L70): 100.000 h; Lifetime LED according to IEC-62717 (L80): 68.000 h; Levensduur LED volgens IES TM-21 (L70): >60.000 h; Lifetime LED according to IES TM-21 (L80): >60.000 h; Fuse protection B10: 41; Fuse protection B16: 65; Fuse protection C10: 67; Fuse protection C16: 108; Basic light level function in per cent: 0 – 100 %; Output: 31 W; Colour Rendering Index CRI: = 82; Photobiological safety in accordance with EN 62471: RG1; Starting current, maximum: 14,8 A; Angle of aperture: 160 °; Detection angle: 360 °; Product category: Sensor-LED-binnenlamp

**Fabrikant** Steinel

**art.nr.** 079185

**Bestelaanduiding** RS PRO 5100 SC 5C 5 Core (5-draads doorvoerbedrading)

Leveren, monteren en bedrijfsklaar instellen