**STEINEL Professional Sensor-LED-binnenlamp**

**RS PRO 5150 SC EM**

**Noodverlichting**

Dimensions (L x W x H): 1500 x 87 x 58 mm; With motion detector: Ja; Manufacturer's Warranty: 5 jaar; With remote control: Ja; Version: Noodverlichting; PU1, EAN: 4007841058715; Colour: grijs; Installation site: wand, plafond; Installation: Plafond; Impact resistance: IK07; IP-rating: IP65; Protection class: II; Ambient temperature: van -20 tot 40 °C; Housing material: kunststof; Cover material: Kunststof gestructureerd; Mains power supply: 220 – 240 V / 50 – 60 Hz; Power consumption: 0,45 W; Mounting height max.: 4,00 m; Detection: evt. door glas, hout en snelbouwwanden; Electronic scalability: Ja; Mechanical scalability: Nee; Reach, radial: Ø 10 m (79 m²); Reach, tangential: Ø 10 m (79 m²); Luminous flux total product: 5940 lm; Colour temperature: 4000 K; Lamp: Led niet vervangbaar; Functions: Gecodeerde communicatie, Buurgroepfunctie, Vrije keuze van de lichtwaarde in een armatuurgroep, Instelbare fade-tijd bij in- en uitschakelen, Aansluiting op centrale batterijsystemen, Bewegingssensor, Lichtsensor, Oriëntatielicht, Noodverlichtings conform EN 60598-2-22 gedurende 3 uur; Twilight setting: 2 – 2000 lx; Time setting: 5 sec. – 60 min; Basic light level function: Ja; Basic light level function time: 1-60 min.; Main light adjustable: 0 - 100 %; Interconnection: Ja; Interconnection via: Bluetooth Mesh; Lifetime LED according to IEC-62717 (L70): 100.000 h; Lifetime LED according to IEC-62717 (L80): 68.000 h; Levensduur LED volgens IES TM-21 (L70): > 60.000 h; Lifetime LED according to IES TM-21 (L80): > 60.000 h; Fuse protection B10: 41; Fuse protection B16: 65; Fuse protection C10: 67; Fuse protection C16: 108; Basic light level function in per cent: 0 – 100 %; Output: 42 W; Luminous flux, emergency light: 706 lm; Photobiological safety in accordance with EN 62471: RG1; Starting current, maximum: 14,8 A; Angle of aperture: 160 °; Detection angle: 360 °; Product category: Sensor-LED-binnenlamp

**Fabrikant** Steinel

**art.nr.** 058715

**Bestelaanduiding** RS PRO 5150 SC EM Noodverlichting

Leveren, monteren en bedrijfsklaar instellen